## Hagatna WWTP
Hagatna Wastewater Treatment Plant
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor | [15 empty] | Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment
| Equipment Name | Asset Class | Asset Number | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional
Process |  |  |  | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No
Pretreatment
catwalk unsafe, poor condition
Primary Treatment | Clarifier 1 | [12 empty] | na | [5 empty] | x |  |  | x |  | x |  | x |  | x | na | [5 empty] | x |  |  | x |  | na |  | x |  | na |  | na |  | na | 1 in service, 2 3 inop | bar: Physical Condition Rating 2; Functionality Rating 2
| Clarifier 2 | [12 empty] | na |  |  |  |  | x |  |  |  | na |  | na |  | x |  | x | na |  |  |  |  | x |  |  |  | na |  | na |  | na |  | na |  | na |  | na | inop | bar: Physical Condition Rating 1; Functionality Rating 0
| Clarifier 3 | [12 empty] | na |  |  |  |  | x |  |  |  | na |  | na |  | x |  | x | na |  |  |  |  | x |  |  |  | na |  | na |  | na |  | na |  | na |  | na | inop | bar: Physical Condition Rating 1; Functionality Rating 0
| Sludge Pump 1 | [12 empty] | na |  |  | x |  | inop |  |  | inop | na | inop |  |  | x |  | x | na |  |  | x |  | inop |  |  |  | na |  | na |  | na |  | x |  | x |  | x | (raw sludge pump) - inop | bar: Physical Condition Rating 0; Functionality Rating 0
| Sludge Pump 2 | [12 empty] | na |  |  | x |  | x |  |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na | x |  | x |  |  | x | (raw sludge pump) | bar: Physical Condition Rating 1; Functionality Rating 1
| Sludge Pump 3 | [12 empty] | na |  |  | x |  |  | x |  |  | na |  | na |  | x |  | x | na |  | x |  |  |  | x |  |  | na |  | na |  | na |  | x | na |  |  | x | (raw sludge pump) | bar: Physical Condition Rating 2; Functionality Rating 2
| Sludge Pump 4 | [12 empty] | na |  |  | x |  |  | x |  |  | na |  | na |  | x |  | x | na |  | x |  |  |  | x |  |  | na |  | na |  | na |  | x | na |  |  | x | (raw sludge pump) | bar: Physical Condition Rating 2; Functionality Rating 2
| Sludge Pump 5 | [12 empty] | na |  |  | x | [5 empty] | na |  | na |  | x |  | x | na |  |  | x | [5 empty] | na |  | na |  | na |  | x | na |  |  | x | scum pump, grinder inop | bar: Physical Condition Rating 1; Functionality Rating 0
Digestion | Aerobic Digester 1 | bar: Physical Condition Rating 1; Functionality Rating 0
Aerobic Digester 2 | bar: Physical Condition Rating 1; Functionality Rating 0
Aerobic Digester 3 | bar: Physical Condition Rating 2; Functionality Rating 2
Aerobic Digester 4 | bar: Physical Condition Rating 3; Functionality Rating 2
| thickener tank | [48 empty] | ozone inop decades | bar: Physical Condition Rating 2; Functionality Rating 2
| Centrifuge Feed Pump 1 | [15 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 0
| Centrifuge Feed Pump 2 | [15 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 2
Thickening | Thickener Feed Pump 1 | [15 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 0
chemical feed | Thickener Feed Pump 2 | [15 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 0
Thickening Tank 1 | bar: Physical Condition Rating 1; Functionality Rating 0
Thickening Tank 2 | bar: Physical Condition Rating 1; Functionality Rating 0
Dewatering | Centrifuge 1 | [12 empty] | na |  | x |  |  | inop |  |  |  | na |  | na |  | x |  | x | na |  | x |  |  | x |  |  |  | na |  | na |  | na |  | x |  | x |  | x | not worth saving | bar: Physical Condition Rating 1; Functionality Rating 0
| Centrifuge 2 | [12 empty] | na |  | x |  |  | inop |  |  |  | na |  | na |  | x |  | x | na |  | x |  |  | x |  |  |  | na |  | na |  | na |  | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 0
| Dewatering Pump 1 | [12 empty] | na | bar: Physical Condition Rating 2; Functionality Rating 2
| Dewatering Pump 2 | [12 empty] | na | bar: Physical Condition Rating 1; Functionality Rating 2
Effluent Pumping | Pump 1 | [12 empty] | na |  |  |  |  | inop |  |  |  | na |  | na |  | x |  | x | na |  | x |  |  | na |  |  |  | na |  | na |  | na |  | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 0
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x | x |  | x |  | x |  |  | x | bar: Physical Condition Rating 1; Functionality Rating 1
Effluent Disposal | Diffuser
Outfall
Odor Control | Blower | bar: Physical Condition Rating 0; Functionality Rating 0
2 sump pumps - Pump/Pipe bldg and Centrifuge bldg | [13 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  |  | x |  | x | bar: Physical Condition Rating 2; Functionality Rating 2
Note on E5: bc: Not Applicable
Note on F5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G5: bc: Moderate to high risk of failure.
Note on H5: bc: Visible degradation
Note on I5: bc: Well maintained, like new condition of equipment or structure.
Note on J5: bc: Not Applicable.
Note on K5: bc: Structure or equipment is not currently functioning for its intended use.
Note on L5: bc: Structure or equipment is in service but function is highly impaired.
Note on M5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on P5: bc: Not Applicable.
Note on Q5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on R5: bc: Visible degradation of equipment or structure, but acceptable.
Note on S5: bc: Well maintained, like new condition of equipment or structure.
Note on T5: bc: Excessive
Note on U5: bc: High Life Cycle Costs but acceptable.
Note on V5: bc: Normal.
Note on AF5: bc: Not Applicable.
Note on AG5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on AH5: bc: Visible degradation of equipment or structure, but acceptable.
Note on AI5: bc: Well maintained, like new condition of equipment or structure.
Note on AJ5: bc: Excessive
Note on AK5: bc: High Life Cycle Costs but acceptable.
Note on AL5: bc: Normal.
Note on AS4: bc: Pumps performing near rated capacity (+/- 5%)

## Agat WWTP
Agat Wastewater Treatment Plant
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor | [15 empty] | Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment
| Equipment Name | Asset Class | Asset Number | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional
Process |  |  |  | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No
Effluent Screens | Traveling Screen 1 | [12 empty] | na | x | [5 empty] | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | na |  | x |  | x |  | na |  | na | both offline need realignment out for couple months | bar: Physical Condition Rating 3; Functionality Rating 0
| Traveling Screen 2 | [12 empty] | na | x | [5 empty] | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | na |  | x |  | x |  | na |  | na | bar: Physical Condition Rating 3; Functionality Rating 0
Influent Pumping | Raw Sewage Pump 1 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x | x |  |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | ok | bar: Physical Condition Rating 3; Functionality Rating 3
| Raw Sewage Pump 2 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x | x |  |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | x |  | x |  | good condition but currently not running | bar: Physical Condition Rating 3; Functionality Rating 0
Raw Sewage Pump 3 | bar: Physical Condition Rating 3; Functionality Rating 3
| Sump Pump | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | x |  |  | na | bar: Physical Condition Rating 3; Functionality Rating 3
Secondary Treatment | Aeration Tank | [12 empty] | na |  | x |  |  | x |  |  | x |  | x |  |  | x |  | x | na |  | x |  |  | x |  |  | x |  | na |  |  | x | x |  | na |  | na |  | rake arm | bar: Physical Condition Rating 2; Functionality Rating 2
| Blower 1 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x | x |  | x |  | na |  |  | x |  |  |  | x |  | x |  | na |  | x | x |  | x |  |  | na | Blower 1 & 3 new | bar: Physical Condition Rating 4; Functionality Rating 3
| Blower 2 | [12 empty] | na |  |  | x |  | x |  |  | na |  | na |  |  | x |  | x | na |  |  | x |  | x |  |  |  | na |  | na |  | na |  | x |  | na |  | na | P.O.S. | bar: Physical Condition Rating 1; Functionality Rating 0
| Blower 3 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x | x |  | x |  | na |  |  | x |  |  |  | x |  | x |  | na |  | x | x |  | x |  |  | na | bar: Physical Condition Rating 4; Functionality Rating 3
Clarifier | bar: Physical Condition Rating 3; Functionality Rating 3
Effluent Pumping | Gaan PS #2 Eff Pump 1 | [12 empty] | na |  |  | x |  |  | x |  | na |  |  | na |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x |  | x |  | na | inop | bar: Physical Condition Rating 2; Functionality Rating 0
| Gaan PS #2 Eff Pump 2 | [12 empty] | na |  |  | x |  |  | x |  | na |  |  | na |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x |  | x |  | na | pump 2 operational pending mechanical seals | bar: Physical Condition Rating 2; Functionality Rating 0
| Gaan PS #2 Eff Pump 3 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  |  | x | operational | bar: Physical Condition Rating 3; Functionality Rating 2
| Pump 4 | [48 empty] | These pumps are Pump Station Gaan (Agat #2)
| Pump 5 | [48 empty] | Tony - currently 3 pumps, future 5 pumps?
Disinfection | Tank, Above Ground | [48 empty] | No disinfection
Other | Drying Beds (not aerobic digestion) | [12 empty] | na | x | [5 empty] | x | na |  | na |  | na |  | na |  | na | x | [5 empty] | na |  | na |  | na |  | na |  | na |  | na |  | na | Drying beds, gravity flow | bar: Physical Condition Rating 2; Functionality Rating 2
Additional from Terry's notes | Drying beds underdrains | bar: Physical Condition Rating 2; Functionality Rating 2
| Ball gear drive | noisy, no guard | bar: Physical Condition Rating 1; Functionality Rating 2
flow meter | bar: Physical Condition Rating 2; Functionality Rating 2
Propeller meter | bar: Physical Condition Rating 2; Functionality Rating 2
Note on E5: bc: Not Applicable
Note on F5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G5: bc: Moderate to high risk of failure.
Note on H5: bc: Visible degradation
Note on I5: bc: Well maintained, like new condition of equipment or structure.
Note on J5: bc: Not Applicable.
Note on K5: bc: Structure or equipment is not currently functioning for its intended use.
Note on L5: bc: Structure or equipment is in service but function is highly impaired.
Note on M5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on P5: bc: Not Applicable.
Note on Q5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on R5: bc: Visible degradation of equipment or structure, but acceptable.
Note on S5: bc: Well maintained, like new condition of equipment or structure.
Note on T5: bc: Excessive
Note on U5: bc: High Life Cycle Costs but acceptable.
Note on V5: bc: Normal.
Note on V6: Terry A. Price: Both screens fairly new, but earthquake caused out-of-alignment issue. Been out of commissioning for couple of months.
Note on AF5: bc: Not Applicable.
Note on AG5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on AH5: bc: Visible degradation of equipment or structure, but acceptable.
Note on AI5: bc: Well maintained, like new condition of equipment or structure.
Note on AJ5: bc: Excessive
Note on AK5: bc: High Life Cycle Costs but acceptable.
Note on AL5: bc: Normal.
Note on AS4: bc: Pumps performing near rated capacity (+/- 5%)

## Baza Gardens WWTP
Baza Gardens Wastewater Treatment Plant
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor | [15 empty] | Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment
| Equipment Name | Asset Class | Asset Number | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional
Process |  |  |  | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No
Pretreatment
- Grit Removal | Pump, Air Lift | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x | x |  |  | x | na |  |  | x |  |  |  | x |  | x |  | na |  | x | x |  |  | x |  | na | bar: Physical Condition Rating 4; Functionality Rating 4
Tank, Above Ground
- Screening | Comminutor | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | na |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
Secondary Treatment | Blower 1 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x | x |  |  | x | na |  |  |  | x |  |  | x |  | x |  | na |  | x | x |  | x |  |  | na | bar: Physical Condition Rating 4; Functionality Rating 4
| Blower 2 | [12 empty] | na |  |  |  | x |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | na |  | x | x |  | x |  |  | na | bar: Physical Condition Rating 3; Functionality Rating 3
| Blower 3 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x | x |  |  | x | na |  |  |  | x |  |  | x |  | x |  | na |  | x | x |  | x |  |  | na | bar: Physical Condition Rating 4; Functionality Rating 4
| Clarifier | [12 empty] | na |  |  | x |  |  | x |  | x |  | x |  |  | x |  | x | na |  | x |  |  | x |  |  | x |  |  |  | x |  | x |  | x |  |  | na | bar: Physical Condition Rating 1; Functionality Rating 1
Effluent Disposal | Meter, Default | [48 empty] | Parshall Flume | bar: Physical Condition Rating 2; Functionality Rating 2
Outfall, Default
Disinfection | CL Ejectors | [12 empty] | na | na |  |  |  |  | x |  | na |  | na |  | na |  | na |  | na | na |  |  |  |  | x |  | na |  | na |  | na |  | x |  | na |  | na | bar: Physical Condition Rating 3; Functionality Rating 3
CL Scale 1 | bar: Physical Condition Rating 2; Functionality Rating 2
CL Scale 2 | bar: Physical Condition Rating 2; Functionality Rating 2
| HVAC, Default | [12 empty] | na | bar: Physical Condition Rating 1; Functionality Rating 0
| Cl2 gas detectors | [12 empty] | na | x | [5 empty] | x | na |  | na |  | na |  |  | na | na | x | [5 empty] | x | na |  |  |  |  | na | x |  |  | na |  | na | bar: Physical Condition Rating 3; Functionality Rating 3
Electrical Generation | Alternator
| Generator (250 kW) | [12 empty] | na |  |  | x |  | x |  |  | na |  | na |  | na |  |  | x | na |  |  | x |  | x |  |  | na |  |  | na |  | na |  | x |  | x |  | na | bar: Physical Condition Rating 1; Functionality Rating 0
Note on B26: Unsure if the genset is GWA or not.
Note on E5: bc: Not Applicable
Note on F5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G5: bc: Moderate to high risk of failure.
Note on H5: bc: Visible degradation
Note on I5: bc: Well maintained, like new condition of equipment or structure.
Note on J5: bc: Not Applicable.
Note on K5: bc: Structure or equipment is not currently functioning for its intended use.
Note on L5: bc: Structure or equipment is in service but function is highly impaired.
Note on M5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on P5: bc: Not Applicable.
Note on Q5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on R5: bc: Visible degradation of equipment or structure, but acceptable.
Note on S5: bc: Well maintained, like new condition of equipment or structure.
Note on T5: bc: Excessive
Note on U5: bc: High Life Cycle Costs but acceptable.
Note on V5: bc: Normal.
Note on Y14: Motor was VERY hot!
Note on AF5: bc: Not Applicable.
Note on AG5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on AH5: bc: Visible degradation of equipment or structure, but acceptable.
Note on AI5: bc: Well maintained, like new condition of equipment or structure.
Note on AJ5: bc: Excessive
Note on AK5: bc: High Life Cycle Costs but acceptable.
Note on AL5: bc: Normal.
Note on AS4: bc: Pumps performing near rated capacity (+/- 5%)

## Inarajan WWTP
Inarajan Wastewater Treatment Plant
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor | [15 empty] | Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment
|  |  |  | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional
Process | Equipment Name | Asset Class | Asset Number | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No
Secondary Treatment | Pond 1 | [12 empty] | na | na | [5 empty] | x |  | na |  | na |  | na |  | na | na | na | [5 empty] | na |  | na |  | na |  | na |  | na |  | na |  | na | in service, aerated, aerator running | bar: Physical Condition Rating 3; Functionality Rating 3
| Pond 2 | [12 empty] | na | na | [5 empty] | x |  | na |  | na |  | na |  | na | na | na | [5 empty] | na |  | na |  | na |  | na |  | na |  | na |  | na | in service, aerated, aerator running | bar: Physical Condition Rating 3; Functionality Rating 3
| Pond 3 | [12 empty] | na | na | [5 empty] | x |  | na |  | na |  | na |  | na | na | na | [5 empty] | na |  | na |  | na |  | na |  | na |  | na |  | na | in service, aerated, motor burnt/not running | bar: Physical Condition Rating 3; Functionality Rating 3
| Pond 4 | [12 empty] | na | na |  |  |  |  | x |  |  | na |  | na |  | na |  | na | na | na | [5 empty] | na |  | na |  | na |  | na |  | na |  | na |  | na | not used | bar: Physical Condition Rating 3; Functionality Rating 0
Sampling Point
Effluent Disposal
- Metering/Diverter Box | Meter | [48 empty] | none of these other pieces of equipment were evaluated
Tank, DIV 1
Tank, DIV 2
Tank, Meter
| Valve, Plug 1 | [12 empty] | na | na |  |  |  | na |  |  | na |  |  | na |  | na |  | na | na | na | [5 empty] | na |  | na |  | na |  | na | na |  |  | na |  |  | all valves need replacing | bar: Physical Condition Rating 1; Functionality Rating 2
| Valve, Plug 2 | [12 empty] | na | na |  |  |  | na |  |  | na |  |  | na |  | na |  | na | na | na | [5 empty] | na |  | na |  | na |  | na | na |  |  | na | bar: Physical Condition Rating 1; Functionality Rating 2
- Percolation Basins | Basin 1
Basin 2
Basin 3
Dewatering | Bed 1 | [48 empty] | gravity flow to drying beds (irrigation, grassy)
Bed 2
Bed 3
Bed 4
Bed 5
Bed 6
Generator - GWA - down since 1989 | bar: Physical Condition Rating 1; Functionality Rating 0
Note on E5: bc: Not Applicable
Note on F5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G5: bc: Moderate to high risk of failure.
Note on H5: bc: Visible degradation
Note on I5: bc: Well maintained, like new condition of equipment or structure.
Note on J5: bc: Not Applicable.
Note on J10: .: One lagoon out of service. Unsure which one is in repair status.
Note on K5: bc: Structure or equipment is not currently functioning for its intended use.
Note on L5: bc: Structure or equipment is in service but function is highly impaired.
Note on M5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on P5: bc: Not Applicable.
Note on Q5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on R5: bc: Visible degradation of equipment or structure, but acceptable.
Note on S5: bc: Well maintained, like new condition of equipment or structure.
Note on T5: bc: Excessive
Note on U5: bc: High Life Cycle Costs but acceptable.
Note on V5: bc: Normal.
Note on AF5: bc: Not Applicable.
Note on AG5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on AH5: bc: Visible degradation of equipment or structure, but acceptable.
Note on AI5: bc: Well maintained, like new condition of equipment or structure.
Note on AJ5: bc: Excessive
Note on AK5: bc: High Life Cycle Costs but acceptable.
Note on AL5: bc: Normal.
Note on AS4: bc: Pumps performing near rated capacity (+/- 5%)

## Northern WWTP
Northern Wastewater Treatment Plant
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor | [15 empty] | Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment
| Equipment Name | Asset Class | Asset Number | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional
Process |  |  |  | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No
all out of service, flow through, trucks pump scum
Pretreatment | Aeration Tank | [12 empty] | na | na | [34 empty] | no scum removal | bar: Physical Condition Rating 1; Functionality Rating 1
| Blower 1 | [12 empty] | 0 |  |  | x | [9 empty] | x | [19 empty] | x |  | x | New blowers, not used yet, waiting delivery of panels MCC | bar: Physical Condition Rating 4 to Functionality Rating 0
| Blower 2 | [12 empty] | 0 |  |  | x | [9 empty] | x | [19 empty] | x |  | x | New blowers, not used yet, waiting delivery of panels MCC | bar: Physical Condition Rating 4 to Functionality Rating 0
| Degritting Tank1 | [12 empty] | na | [11 empty] | na | [23 empty] | not working, flow through | bar: Physical Condition Rating 1; Functionality Rating 0
| Degritting Tank2 | [12 empty] | 0 | [11 empty] | na | [23 empty] | refurbished not in service yet | bar: Physical Condition Rating 1; Functionality Rating 0
| Grit Removal | [12 empty] | na |  |  |  | x | [31 empty] | no scum removal | bar: Physical Condition Rating 4 to Functionality Rating 0
| Mixing Tank | [12 empty] | na | [11 empty] | na | [23 empty] | gates need refurbishing | bar: Physical Condition Rating 2; Functionality Rating 2
| Screening, comminutor | [12 empty] | 0 | [12 empty] | x | [22 empty] | removed | bar: Physical Condition Rating 0; Functionality Rating 0
| ozonator | [12 empty] | na | [11 empty] | na | [23 empty] | unit removed | bar: Physical Condition Rating 0; Functionality Rating 0
Primary Treatment | Clarifier 1 | [12 empty] | na | [12 empty] | x | [22 empty] | has not been refurbished. Sections of weirs missing. | bar: Physical Condition Rating 1; Functionality Rating 1
| Clarifier 2 | [12 empty] | na | [12 empty] | x | [22 empty] | recently refurbished, rak edrive needs recoating | bar: Physical Condition Rating 2; Functionality Rating 2
| Primary Sludge Pump 1 | [12 empty] | na |  |  | x | [5 empty] | na |  | na | x |  |  | ? | na |  |  | x | [5 empty] | na |  | na |  | na |  | na |  | na |  | na | pumps 1, 3, 4 are out, 2 functional | bar: Physical Condition Rating 0; Functionality Rating 0
| Primary Sludge Pump 2 | [12 empty] | na |  |  | x | [5 empty] | x |  | x | x |  |  | ? | na |  |  | x | [5 empty] | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| Primary Sludge Pump 3 | [12 empty] | na |  |  | x | [5 empty] | na |  | na | x |  |  | ? | na |  |  | x | [5 empty] | na |  | na |  | na |  | na |  | na |  | na | bar: Physical Condition Rating 0; Functionality Rating 0
| Primary Sludge Pump 4 | [12 empty] | na |  |  | x | [5 empty] | na |  | na | x |  |  | ? | na |  |  | x | [5 empty] | na |  | na |  | na |  | na |  | na |  | na | bar: Physical Condition Rating 0; Functionality Rating 0
| sludge grinder 1 | [12 empty] | na |  |  | x | [5 empty] | na |  | na |  | x |  | x | na |  |  | x | [5 empty] | na |  | na |  | na |  | na |  | na |  | na | functionality 0, to be removed | bar: Physical Condition Rating 2; Functionality Rating 0
| sludge grinder 2 | [12 empty] | na |  |  | x | [5 empty] | na |  | na |  | x |  | x | na |  |  | x | [5 empty] | na |  | na |  | na |  | na |  | na |  | na | to be replaced by chopper pumps (1, 2, 3, 4) | bar: Physical Condition Rating 2; Functionality Rating 0
| sludge grinder 3 | [12 empty] | na |  |  | x | [5 empty] | na |  | na |  | x |  | x | na |  |  | x | [5 empty] | na |  | na |  | na |  | na |  | na |  | na | functionality 0, to be removed | bar: Physical Condition Rating 2; Functionality Rating 0
| sludge grinder 4 | [12 empty] | na |  |  | x | [5 empty] | na |  | na |  | x |  | x | na |  |  | x | [5 empty] | na |  | na |  | na |  | na |  | na |  | na | to be replaced by chopper pumps (1, 2, 3, 4) | bar: Physical Condition Rating 2; Functionality Rating 0
| Scum Pump 1 | [12 empty] | na |  |  |  | x | annual |  |  |  | x |  | x |  | x |  | ? | na |  |  |  | x | x |  |  |  | x |  | x |  | x | x |  | na |  |  | na | functional, to be replaced soon | bar: Physical Condition Rating 2; Functionality Rating 2
| Scum Pump 2 | [12 empty] | 0 |  |  |  | x |  |  | na |  | na |  | na | x |  |  | ? | 0 |  |  |  | x |  |  | na |  | na |  | na |  | na |  | na | na |  |  | na | refurbished, soon to be tested | bar: Physical Condition Rating 3; Functionality Rating 0
| Sludge Recirculation Pump 1 | [12 empty] | na | [12 empty] | x | [22 empty] | existing | bar: Physical Condition Rating 2; Functionality Rating 2
| Sludge Recirculation Pump 2 | [12 empty] | na | [12 empty] | x | [22 empty] | existing | bar: Physical Condition Rating 2; Functionality Rating 2
| sump pump | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 2; Functionality Rating 2
Disinfection | Meter, Default | [12 empty] | na | bar: Physical Condition Rating 0; Functionality Rating 0
| chlorine contact basin | [12 empty] | na | bar: Physical Condition Rating 1; Functionality Rating 0
| effluent pumps 1, 2 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 0; Functionality Rating 0
| scum pump, 1, 2 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 0; Functionality Rating 0
Digestion | Boiler | [12 empty] | na | [12 empty] | x | [22 empty] | out of service, not used | bar: Physical Condition Rating 1; Functionality Rating 0
- Primary Anaerobic Digestion | Blower, GAS EX | [12 empty] | na | [12 empty] | x | [22 empty] | needs to be replaced | bar: Physical Condition Rating 0; Functionality Rating 0
| centrate well | [12 empty] | na | [11 empty] | na | [23 empty] | 2 submersed pumps, #2 pump inoperable | bar: Physical Condition Rating 2; Functionality Rating 2
| pump 1 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 2; Functionality Rating 2
| pump 2 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 0
| Motor, GAS EX | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 0; Functionality Rating 0
| Tank, Mid-Grade | [12 empty] | na | [11 empty] | na
| Recirculation Pump 1 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 2; Functionality Rating 2
| Recirculation Pump 2 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 2; Functionality Rating 2
| sump pump1 | [12 empty] | na | [12 empty] | x | [22 empty] | original | bar: Physical Condition Rating 2; Functionality Rating 2
| water seal pump1 | [12 empty] | na | [12 empty] | x | [22 empty] | inoperable | bar: Physical Condition Rating 0; Functionality Rating 0
| water seal pump 2 | [12 empty] | na | [12 empty] | x | [22 empty] | inoperable | bar: Physical Condition Rating 0; Functionality Rating 0
| digestor mechanical mixer 1, 2, 3, 4 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 0; Functionality Rating 0
- Secondary Anaerobic Digestor | Blower, GAS EX | [12 empty] | na | [11 empty] | na | [23 empty] | needs to be replaced | bar: Physical Condition Rating 0; Functionality Rating 0
| Motor, GAS EX | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 0; Functionality Rating 0
| Tank, Mid-Grade | [12 empty] | na | [11 empty] | na
| digestor transfer pumps 1 | [12 empty] | na | [12 empty] | x | [22 empty] | inop out of service, stater problems | bar: Physical Condition Rating 0; Functionality Rating 0
| digestor transfer pumps 2 | [12 empty] | na | [12 empty] | x | [22 empty] | working | bar: Physical Condition Rating 2; Functionality Rating 2
| digestor mechanical mixer 1, 2, 3, 4 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 0; Functionality Rating 0
Dewatering | Centrifuge 1 | [12 empty] | na | [12 empty] | x | [22 empty] | inop | bar: Physical Condition Rating 1; Functionality Rating 0
| Centrifuge 2 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 0
| hoist | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 1; Functionality Rating 0
| Centrifuge Feed Pump 1 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 0
| Centrifuge Feed Pump 2 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 2; Functionality Rating 2
| polymer pump and motor | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 0
| polymer chemical feed pumps 1, 2 | [12 empty] | na | [12 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 0
| Drying Bed 1 | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 3
| Drying Bed 2 | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 3
| Drying Bed 3 | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 3
| Drying Bed 4 | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 3
| Drying Bed 5 | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 3
| Drying Bed 6 | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 3
| Drying Bed 7 | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 3
| Drying Bed 8 | [12 empty] | na | [11 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 3
| chemical feed Thickener Feed Pump 1 | [12 empty] | na | bar: Physical Condition Rating 1; Functionality Rating 1
| chemical feed Thickener Feed Pump 2 | [12 empty] | na | bar: Physical Condition Rating 1; Functionality Rating 1
| chemical feed tanksThickening Mixing Tank 1 | [12 empty] | na | bar: Physical Condition Rating 1; Functionality Rating 1
| chemical feed tanks Thickening Mixing Tank 2 | [12 empty] | na | bar: Physical Condition Rating 1; Functionality Rating 1
Electrical Generation | [13 empty] | na |  |  |  | x |  |  | x |  | x |  | x | [24 empty] | working, good | bar: Physical Condition Rating 3; Functionality Rating 3
Note on E5: bc: Not Applicable
Note on F5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G5: bc: Moderate to high risk of failure.
Note on H5: bc: Visible degradation
Note on I5: bc: Well maintained, like new condition of equipment or structure.
Note on J5: bc: Not Applicable.
Note on K5: bc: Structure or equipment is not currently functioning for its intended use.
Note on L5: bc: Structure or equipment is in service but function is highly impaired.
Note on M5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on P5: bc: Not Applicable.
Note on Q5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on R5: bc: Visible degradation of equipment or structure, but acceptable.
Note on S5: bc: Well maintained, like new condition of equipment or structure.
Note on T5: bc: Excessive
Note on U5: bc: High Life Cycle Costs but acceptable.
Note on V5: bc: Normal.
Note on AF5: bc: Not Applicable.
Note on AG5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on AH5: bc: Visible degradation of equipment or structure, but acceptable.
Note on AI5: bc: Well maintained, like new condition of equipment or structure.
Note on AJ5: bc: Excessive
Note on AK5: bc: High Life Cycle Costs but acceptable.
Note on AL5: bc: Normal.
Note on AS4: bc: Pumps performing near rated capacity (+/- 5%)

## Umatac-Merzio WWTP
Umatac-Merizo Wastewater Treatment Plant
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor | [15 empty] | Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment
| Equipment Name | Asset Class | Asset Number | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional
|  |  |  | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No
Process
This building considered Pump Station #13
Influent Pumping | Electrical Generator | [48 empty] | GPA genset - not evaluated
| Parshal Flume Q meter | [12 empty] | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | na | na |  |  | x |  |  | x |  |  | na |  | na |  | na | x |  |  | na |  | na | parshall flume | bar: Physical Condition Rating 3; Functionality Rating 2
| Pump 1 | [12 empty] | na |  |  | x |  |  | x |  | x |  | x |  |  | x |  | x | na |  |  | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  |  | x | motor rewound, vibration guide piping broken | bar: Physical Condition Rating 3; Functionality Rating 2
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  | na |  | na |  |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x |  | na |  | x | bar: Physical Condition Rating 3; Functionality Rating 0
| Wet Well | [12 empty] | na | [35 empty] | covered wet pit (sub pumps) | bar: Physical Condition Rating 3; Functionality Rating 3
Secondary Treatment | Mixer 1 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| Mixer 2 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| Pond, Lagoon | [48 empty] | 14 ft deep, two cells, hydraulically overloaded, circulation poor, never drained and cleaned | bar: Physical Condition Rating 3; Functionality Rating 2
Booster Pumping | Pump 1 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  |  | x |  | x | in service, needs seals, leaking | bar: Physical Condition Rating 2; Functionality Rating 3
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  |  | na |  | na |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x |  | na |  | na | bar: Physical Condition Rating 1; Functionality Rating 0
Effluent Pumping | Electrical Generator | [48 empty] | GPA genset
| Pump 1 | [12 empty] | na | [5 empty] | x |  |  | x |  | x |  | x |  | x | na | [5 empty] | x |  |  | x |  | x |  | x | x |  | x |  | x |  | PS 20, only viewed from car did not visit due to goat family | bar: Physical Condition Rating 3; Functionality Rating 3
| Wet Well | [48 empty] | Pump rating based on Bill's word, he says pump rewound
Effluent Disposal | Overflow Basin 1 | bar: Physical Condition Rating 3; Functionality Rating 3
Overflow Basin 2 | bar: Physical Condition Rating 3; Functionality Rating 3
Note on E5: bc: Not Applicable
Note on F5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G5: bc: Moderate to high risk of failure.
Note on H5: bc: Visible degradation
Note on I5: bc: Well maintained, like new condition of equipment or structure.
Note on J5: bc: Not Applicable.
Note on K5: bc: Structure or equipment is not currently functioning for its intended use.
Note on L5: bc: Structure or equipment is in service but function is highly impaired.
Note on M5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on P5: bc: Not Applicable.
Note on Q5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on R5: bc: Visible degradation of equipment or structure, but acceptable.
Note on S5: bc: Well maintained, like new condition of equipment or structure.
Note on T5: bc: Excessive
Note on U5: bc: High Life Cycle Costs but acceptable.
Note on V5: bc: Normal.
Note on AF5: bc: Not Applicable.
Note on AG5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on AH5: bc: Visible degradation of equipment or structure, but acceptable.
Note on AI5: bc: Well maintained, like new condition of equipment or structure.
Note on AJ5: bc: Excessive
Note on AK5: bc: High Life Cycle Costs but acceptable.
Note on AL5: bc: Normal.
Note on AS4: bc: Pumps performing near rated capacity (+/- 5%)

## Ugum WTP
Ugum Water Treatment Plant
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor | [15 empty] | Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment
| Equipment Name | Asset Class | Asset Number | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional
|  |  |  | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No
Process
Intake | Pipe | [48 empty] | could not see pipe | bar: Physical Condition Rating 2; Functionality Rating 2
| Raw Water Pump 1 | [12 empty] | 28161 |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | 28161 |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x |  | x | x |  | leaking seal water | all motor coatings poor, all pipes very rusty | bar: Physical Condition Rating 2; Functionality Rating 2
| Raw Water Pump 2 | [12 empty] | 39100 |  |  | x |  |  |  | x |  | x |  | x | x |  |  | x | 39100 |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | x |  | x |  | motor gone, to be installed, pump refurbished | bar: Physical Condition Rating 3; Functionality Rating 0
| Raw Water Pump 3 | [12 empty] | 48953 |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | 48953 |  |  | x |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | runtime hours may not be accurate | bar: Physical Condition Rating 2; Functionality Rating 1
| Screening | [48 empty] | problem with ducks on top of screen | bar: Physical Condition Rating 2; Functionality Rating 2
Tank | bar: Physical Condition Rating 2; Functionality Rating 2
Flocculation | Tank 1 | bar: Physical Condition Rating 2; Functionality Rating 2
Tank 2 | bar: Physical Condition Rating 2; Functionality Rating 2
Tank 3 | bar: Physical Condition Rating 2; Functionality Rating 2
Tank 4 | bar: Physical Condition Rating 2; Functionality Rating 2
| Mixer, Rapid | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | na |  | x | x |  | na |  | na |  | 8 mixers, all work | bar: Physical Condition Rating 2; Functionality Rating 2
| Motor, Rapid - see Mixer above | [15 empty] | x | bar: Physical Condition Rating 2; Functionality Rating 3
Sedimentation | Settling Tank 1 | [12 empty] | na |  | x |  |  |  | x |  |  | x |  | x |  | x |  | x | na |  | x |  |  |  | x |  |  | x |  | na |  | x | x |  | na |  | na |  | tube settlers poor | motor bases condition 1 | bar: Physical Condition Rating 2; Functionality Rating 2
| Settling Tank 2 | [12 empty] | na |  | x |  |  |  | x |  |  | na | na |  |  | x |  | x | na |  | x |  |  |  | x |  |  | na |  | na |  | na |  | x | na |  | na |  | tube settlers poor, rake out of service (motor ok) | bar: Physical Condition Rating 2; Functionality Rating 0
| Settling Tank 3 | [12 empty] | na |  | x |  |  |  | x |  | x |  |  | x |  | x |  | x | na |  | x |  |  |  | x |  | x |  |  | na |  | x | x |  | na |  | na |  | sludge rake excess vibration (temp normal) | bar: Physical Condition Rating 2; Functionality Rating 2
| Settling Tank 4 | [12 empty] | na |  | x |  |  |  | x |  |  | x |  | x |  | x |  | x | na |  | x |  |  |  | x |  |  | x |  | na |  | x | x |  | na |  | na |  | scum system valves poor (1), telescoping valve out of service, skimmers, rakes, tubes all poor condition | bar: Physical Condition Rating 2; Functionality Rating 2
Filtration | Backwash Pump 1 | [12 empty] | na |  |  | x |  |  | x |  | x |  |  | x |  | x |  | x | na |  |  | x |  |  | x |  | x |  |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
| Backwash Pump 2 | [12 empty] | na |  |  | x |  |  | x |  | x |  |  | x |  | x |  | x | na |  |  | x |  |  | x |  | x |  |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
| Backwash Tank | [48 empty] | exterior coatings 1 | bar: Physical Condition Rating 2; Functionality Rating 3
| Filter Blower | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | na |  | x | x |  | x |  | na | bar: Physical Condition Rating 2; Functionality Rating 3
| Filter Tank 1 | [48 empty] | Filters: ext/int coatings poor, valves inop, however works well especially considering poor floc/set | bar: Physical Condition Rating 1; Functionality Rating 3
| Filter Tank 2 | [48 empty] | 3 media, 72 hr vs. turbidity breakthrough | bar: Physical Condition Rating 1; Functionality Rating 3
| Filter Tank 3 | [48 empty] | flow control all manual | bar: Physical Condition Rating 1; Functionality Rating 3
Filter Tank 4 | bar: Physical Condition Rating 1; Functionality Rating 3
Disinfection | Ejector 1 | [12 empty] | na |  |  | x |  |  |  | x |  | na |  | na |  | na |  | na | na |  |  | x |  |  | x |  |  | na |  | na |  | na | x |  | na |  | na |  | injector rotameter | bar: Physical Condition Rating 3; Functionality Rating 3
| Ejector 2 | [48 empty] | not there | bar: Physical Condition Rating 0; Functionality Rating 0
| Ejector 3 | [48 empty] | set up for 2 ejectors
| Scale | [12 empty] | na |  |  | na |  |  | na |  |  | na |  | na |  | na |  | na | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x | na |  | na |  | they do not use any scale | bar: Physical Condition Rating 1; Functionality Rating 0
| cl2 detector | [12 empty] | na | x |  |  |  | x |  |  |  | na |  | na |  | na |  | na | 0 | x |  |  |  | x |  |  |  | na |  | na |  | na |  | x | na |  | na |  | cl alarm does not work | bar: Physical Condition Rating 1; Functionality Rating 0
Clearwell | Clearwell Discharge Pump 1 | [12 empty] | na |  |  | x |  |  |  | x |  | x | x |  |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | clearwell: strong cl smell | bar: Physical Condition Rating 3; Functionality Rating 3
| Clearwell Discharge Pump 2 | [12 empty] | na |  |  | x |  | x |  |  | x |  | x |  |  | x |  | x | na |  |  | x |  | x |  |  | x |  |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 2; Functionality Rating 2
Reservoir | Reservoir Tank - see WWTP Buildings
Chemical | Chemical Feeder A | [15 empty] | x | [32 empty] | Hoppers | bar: Physical Condition Rating 2; Functionality Rating 2
| Chemical Feeder B | [15 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 2
| Chemical Feeder C | [15 empty] | x | bar: Physical Condition Rating 1; Functionality Rating 2
| Chem Feed Pump Alum | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | na |  | Feed pumps | bar: Physical Condition Rating 2; Functionality Rating 2
| Chem Feed Pump Soda Ash | [12 empty] | na |  |  | x |  |  | x |  |  | na |  | na |  | x |  | x | na |  |  | x |  |  | na |  |  | na |  | na |  | na |  | x |  | x | na | bar: Physical Condition Rating 1; Functionality Rating 0
| Chem Feed Pump Carbon | [12 empty] | na |  |  | x |  |  | x |  |  | na |  | na |  | x |  | x | na |  |  | x |  |  | na |  |  | na |  | na |  | na |  | x |  | x | na | bar: Physical Condition Rating 1; Functionality Rating 0
| Polymer Feeder | [48 empty] | ? Does not exist?
vent system | bar: Physical Condition Rating 0; Functionality Rating 0
equipment lift | bar: Physical Condition Rating 1; Functionality Rating 2
Solids Handling | Centrifuge | [12 empty] | 0 |  | x |  |  | na |  |  |  | na |  | na |  | x |  | x | 0 |  | x |  |  |  | na |  |  | na |  | na |  | na |  | x |  | x | na | bar: Physical Condition Rating 1; Functionality Rating 0
| Centrifuge Feed Pump 1 | [12 empty] | na |  | x |  |  |  | x |  |  | na |  | na |  | x |  | x | na |  |  | x |  |  | na |  |  | na |  | na |  | na |  | x |  | x |  | x | not working | bar: Physical Condition Rating 1; Functionality Rating 0
| Centrifuge Feed Pump 2 | [48 empty] | not there/only 1 pump
| Polymer Feed Pump 1 | [12 empty] | 0 |  |  |  | x |  |  | na |  | na |  | na |  | x |  | x | 0 |  |  |  | x |  |  | na |  | na |  | na |  | na |  | x |  | x |  | x | not working, never used | bar: Physical Condition Rating 1; Functionality Rating 0
| Polymer Feed Pump 2 | [12 empty] | 0 |  |  |  | x |  |  | na |  | na |  | na |  | x |  | x | 0 |  |  |  | x |  |  | na |  | na |  | na |  | na |  | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 0
| Polymer Holding Tank | [48 empty] | ? Does not exist?
| Thickening Feed Pump 1 | [48 empty] | does not exist | bar: Physical Condition Rating 0; Functionality Rating 0
| Thickening Feed Pump 2 | [48 empty] | does not exist | bar: Physical Condition Rating 0; Functionality Rating 0
| Thickening Tank | [48 empty] | sludge storage tank - surface water siphoned off into bushes, see pics | bar: Physical Condition Rating 2; Functionality Rating 2
| Sludge Transfer Pump | [12 empty] | na |  | x |  |  | x |  |  |  | na |  | na |  | x |  | x | na |  | x |  |  | x |  |  |  | na |  | na |  | na |  | x | na |  | na | bar: Physical Condition Rating 1; Functionality Rating 0
Note on E5: bc: Not Applicable
Note on F5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G5: bc: Moderate to high risk of failure.
Note on H5: bc: Visible degradation
Note on I5: bc: Well maintained, like new condition of equipment or structure.
Note on J5: bc: Not Applicable.
Note on K5: bc: Structure or equipment is not currently functioning for its intended use.
Note on L5: bc: Structure or equipment is in service but function is highly impaired.
Note on M5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on P5: bc: Not Applicable.
Note on Q5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on R5: bc: Visible degradation of equipment or structure, but acceptable.
Note on S5: bc: Well maintained, like new condition of equipment or structure.
Note on T5: bc: Excessive
Note on U5: bc: High Life Cycle Costs but acceptable.
Note on V5: bc: Normal.
Note on AF5: bc: Not Applicable.
Note on AG5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on AH5: bc: Visible degradation of equipment or structure, but acceptable.
Note on AI5: bc: Well maintained, like new condition of equipment or structure.
Note on AJ5: bc: Excessive
Note on AK5: bc: High Life Cycle Costs but acceptable.
Note on AL5: bc: Normal.
Note on AS4: bc: Pumps performing near rated capacity (+/- 5%)
Note on AT10: .: New pump installation. Not on line yet.

## WWTP Buildings
GWA Wastewater Treatment Plant - Buildings
| Condition and Functionality Rating | [9 empty] | Superstructure Building | [41 empty] | Wet Well | [19 empty] | Wet Well Ventilation |  |  |  | Dry Well Ventilation | [5 empty] | Odor Control |  | Hoist
Pump Station | General Condition Rating |  |  |  |  | General Functionality Rating |  |  |  |  | Exterior Wall Condition |  |  |  |  | Interior Wall Condition |  |  |  |  | Exterior Finish Condition |  |  |  |  | Interior Finish Condition |  |  |  |  | Equipment Finish Condition |  |  |  |  | Roof Condition |  |  |  |  | Window Condition |  |  |  |  | Pipe Support Condition |  |  |  |  | Equipment Access Layout OK |  | Top Slab Condition |  |  |  |  | Interior Wall Condition |  |  |  |  | Hatchway Condition |  |  |  |  | Hatchway Accessible |  |  |  |  | Mechanical Ventilation |  | Separate from Dry Well |  | Mechanical Ventilation |  | Gas Detection Equipment |  | Dehumidification Effective
| 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Yes | No | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Y | N | Y | N | Y | N | Y | N | Y | N | Y | N | Y | N
Northern
northern pretreat bldg 1 |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  |  |  | x | [6 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x
fencing |  |  | x
Pretreatment Building |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  |  |  | x | [6 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x |  |  |  | x |  |  |  |  | x |  |  | na |  |  |  |  | na | [5 empty] | x | x |  |  | x |  | x |  | x |  | x |  | x
Pump Gallery |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x |  | na |  |  |  |  | na |  |  |  |  | na |  |  |  |  | na |  |  |  |  | na |  | na | [8 empty] | x | 1
Digestor Building |  | x |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [33 empty] | 1
Dewatering |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x |  |  |  |  | x |  |  |  | na | [5 empty] | x |  |  |  | x |  | na | [31 empty] | 0
Primary Clarifier Building |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x |  | na |  |  |  |  | na |  |  |  |  | na |  |  |  |  | na | [15 empty] | x
Agana
Primary Clarifiers (3) Covered |  |  |  | x |  |  |  | x | [5 empty] | x |  | na | [7 empty] | x |  | na | [6 empty] | na | [5 empty] | x |  | na |  |  |  |  | na |  |  |  |  | x | [32 empty] | x |  | x
Pump Piping Gallery Bldg |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [34 empty] | x
Centrifuge Bldg |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x
Agat
Wet Pit Bldg |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  |  | x - inop | x |  |  | na |  | x |  | x |  | x |  | x
Clarifier |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | na |  |  |  |  | na | [6 empty] | x |  |  | x | [22 empty] | na |  | na |  | na |  | x |  | x |  | x |  | x
Gaan Pump Station Bldg |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | x | [22 empty] | na |  | na |  | x |  | x |  | x |  | x | 3 |  | nice roof vents directly above
Baza Gardens
Admin Bldg |  | x |  |  |  |  | x | [5 empty] | x | [5 empty] | x |  |  |  | x | [5 empty] | x |  | x | [6 empty] | x |  |  |  |  | x |  |  | x |  |  |  |  | na |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | na |  | na |  |  | x |  | na |  | x |  | x |  | x
Blower Room |  | x |  |  |  |  | x | [5 empty] | x |  |  |  |  | x | x |  |  |  | x |  |  |  |  | x |  |  | x | [5 empty] | x |  |  |  |  | x | [5 empty] | x |  |  | na |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | na |  | na |  |  | x |  | x |  | x |  |  | x
Cl2 Room |  | x |  |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | x |  |  |  |  | x |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | na |  | na |  |  | na | x |  |  | x |  | x |  | x
Treatment plant structure |  | x |  |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x |  | x |  |  |  |  | x | [5 empty] | x |  |  |  | x |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x | na |  |  | x |  | x |  | x |  | x |  | x
Inarajan
Main Control Bldg/Office |  | x | [5 empty] | x | [5 empty] | x |  |  |  | x | [5 empty] | x |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x |  |  |  |  | x |  |  | x |  |  |  | x | [5 empty] | x |  | x |  |  |  |  | x | [5 empty] | x | x |  |  | x |  | x |  | x |  | x
Umatac/Merizo
Maintenance Bldg |  |  |  | x |  |  |  |  | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  | x | [33 empty] | 4
Pump Station 13 |  |  |  | x |  |  |  |  | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x |  |  | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | na |  |  | na |  | na |  | na |  | x | 2 |  | submersible pumps, "boomer" arm hoist
Booster Bldg (PS19) |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | x
Effluent Pumping PS 20 |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  | nd | [7 empty] | x |  | nd |  |  |  |  | nd | [7 empty] | x |  |  |  |  | x |  | nd |  |  |  |  | nd |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  |  | x | na |  |  | na |  | na |  | na |  | x |  | x | only viewed from car, could not approach bldg due to goat family, GPA genset, one submersible pump
Ugum
Intake genset bldg |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | x | [35 empty] | door poor
Flocculation structure |  |  | x | [5 empty] | x |  |  | x | [5 empty] | x - interior of floc tanks |  |  |  | x | [5 empty] | x |  |  |  | x | [5 empty] | x - walkway slab |  |  | na | [7 empty] | x |  | x | [34 empty] | x
sed basins (same structure as floc) |  |  | x | [5 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x - walkway slab |  |  | na | [6 empty] | x |  |  | x | [34 empty] | x
control room (same struc as floc) |  |  | x | [5 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x |  |  |  | x | [5 empty] | x |  |  |  | x |  |  | x
pipe gallery (under floc struc) |  | x | [6 empty] | x |  | na | [5 empty] | x |  |  |  | na | [5 empty] | x |  |  |  |  | x |  |  |  | na |  |  |  |  | na | [5 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | na |  | na |  | na |  | na |  |  | x |  |  | clearwell in pump gallery, strong CL2 smell, stairs from control room poor/railing very dangerous (see pic)
centrifuge bldg/chem bldg |  |  | x | [5 empty] | x |  |  | x | [5 empty] | x |  |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x |  |  |  | x | [5 empty] | x |  |  | x | [33 empty] | 1
blower room |  |  | x | [5 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x | [5 empty] | x |  |  |  | x |  |  | na | [5 empty] | x | [5 empty] | x |  |  | x | [35 empty] | connected to above
chlorine room |  | x | [6 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  | na | [5 empty] | x |  |  |  |  | x |  |  |  | x | [33 empty] | 2 |  | doors not secure, falling off
Reservoir |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | nd | [5 empty] | x |  |  |  | nd | [6 empty] | x |  |  |  | x |  |  |  | na | [6 empty] | x |  |  | na | [35 empty] | roof collapsed, not sure why (maybe suction) - see pic
Note on B6: bc: Not Applicable
Note on C6: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on D6: bc: Moderate to high risk of failure.
Note on E6: bc: Visible degradation of equipment or structure, but acceptable.
Note on F6: bc: Well maintained, like new condition of equipment or structure.
Note on G6: bc: Not Applicable.
Note on H6: bc: Structure or equipment is not currently functioning for its intended use.
Note on I6: bc: Structure or equipment is in service but function is highly impaired.
Note on J6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on K6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on L6: bc: Not Applicable.
Note on M6: bc: Structure or equipment is not currently functioning for its intended use.
Note on N6: bc: Structure or equipment is in service but function is highly impaired.
Note on O6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on P6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on Q6: bc: Not Applicable.
Note on R6: bc: Structure or equipment is not currently functioning for its intended use.
Note on S6: bc: Structure or equipment is in service but function is highly impaired.
Note on T6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on U6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on V6: bc: Not Applicable.
Note on W6: bc: Structure or equipment is not currently functioning for its intended use.
Note on X6: bc: Structure or equipment is in service but function is highly impaired.
Note on Y6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on Z6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AA6: bc: Not Applicable.
Note on AB6: bc: Structure or equipment is not currently functioning for its intended use.
Note on AC6: bc: Structure or equipment is in service but function is highly impaired.
Note on AD6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AE6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AF6: bc: Not Applicable.
Note on AG6: bc: Structure or equipment is not currently functioning for its intended use.
Note on AH6: bc: Structure or equipment is in service but function is highly impaired.
Note on AI6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AJ6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AK6: bc: Not Applicable.
Note on AL6: bc: Structure or equipment is not currently functioning for its intended use.
Note on AL30: Roof in very poor condition
Note on AM6: bc: Structure or equipment is in service but function is highly impaired.
Note on AN6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AO6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AP6: bc: Not Applicable.
Note on AQ6: bc: Structure or equipment is not currently functioning for its intended use.
Note on AQ30: Windows essentially non-existent
Note on AR6: bc: Structure or equipment is in service but function is highly impaired.
Note on AS6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AT6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AU6: bc: Not Applicable.
Note on AV6: bc: Structure or equipment is not currently functioning for its intended use.
Note on AW6: bc: Structure or equipment is in service but function is highly impaired.
Note on AX6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AY6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AZ6: bc: Not Applicable.
Note on BA6: bc: Structure or equipment is not currently functioning for its intended use.
Note on BB6: bc: Not Applicable.
Note on BC6: bc: Structure or equipment is not currently functioning for its intended use.
Note on BD6: bc: Structure or equipment is in service but function is highly impaired.
Note on BE6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BF6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BG6: bc: Not Applicable.
Note on BH6: bc: Structure or equipment is not currently functioning for its intended use.
Note on BI6: bc: Structure or equipment is in service but function is highly impaired.
Note on BJ6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BK6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BL6: bc: Not Applicable.
Note on BM6: bc: Structure or equipment is not currently functioning for its intended use.
Note on BN6: bc: Structure or equipment is in service but function is highly impaired.
Note on BO6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BP6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BQ6: bc: Not Applicable.
Note on BR6: bc: Structure or equipment is not currently functioning for its intended use.
Note on BS6: bc: Structure or equipment is in service but function is highly impaired.
Note on BT6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BU6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.